## Conductored Cables
Part Number | Description | Cable Type | # of Condctors | AWG Size | Stranding | Copper Type | Insulation | Insulation Thickness | Insulation color Code | Shielding | Drain Wire Type | Jacket Type | Jacket Thickness | Nominal Cable O.D. | Jacket Colors | Voltage Rating | Operating Temperature | Flame Test | NEC Rating | RoHS Compliant | Max Pull Tension | Max Bend Radius | Cable Weight | Nominal DCR | Nom. Cap. Between Cond. | Nom. Cap. Cond. To Shield | Applications | Cable Print
2C1P20SP | 4 Cond. 20 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 20 | 7x28 | Bare | Plenum PVC | 0.008 in. | (BK, RD Shld) WH, GN | 2 SH / 2 UNSH | Tinned Copper | Plenum PVC | 0.015 in. | 0.180 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 63 lbs | 1.619 in | 25 lbs | 10.1 Ohms/1000 Ft. | 60 pf/ft | 108 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C1PS20PBK 4/22 Shielded CMP Audio Cable A B C D F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C1P22SP | 4 Cond. 22 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 22 | 7x30 | Bare | Plenum PVC | 0.007 in. | (BK, RD Shld) WH, GN | 2 SH / 2 UNSH | Tinned Copper | Plenum PVC | 0.015 in. | 0.145 in. | BK, WH | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 51 lbs | 1.305 in | 18 lbs | 17.5 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C1PS22PBK 4/22 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C1PS22SP | 4 Cond. 22 AWG Solid Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 22 | Solid | Bare | Plenum PVC | 0.008 in. | (BK, RD Shld) WH, GN | 2 SH / 2 UNSH | Tinned Copper | Plenum PVC | 0.015 in. | 0.145 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 51 lbs | 1.305 in | 18 lbs | 17.5 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C1PS22PSBK 4/22 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
4C1PS22SP | 6 Cond. 22 AWG Solid Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 6 | 22 | Solid | Bare | Plenum PVC | 0.008 in. | (BK, RD Shld) WH, GN, BN, BL | 2 SH / 4 UNSH | Tinned Copper | Plenum PVC | 0.015 in. |  | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes |  |  |  |  | 54 pf/ft | 97 pf/ft | Audio, Control, Low Voltage Power
2C10P | 2 Cond. 10 AWG Strd. Unshielded CL2P | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 10 | 68x28 | Bare | Plenum PVC | 0.012 in. | BK, WH | N/A | N/A | Plenum PVC | 0.015 in. | 0.275 in. | BK | 150 V | 0 to 60 C | NFPA 262 Plenum | CL2P | Yes | 260 lbs | 2.75 in. | 88 lbs | 1.1 Ohms/1000ft. | 28 pf/ft | N/A | Audio, Control, Low Voltage Power
2C12P | 2 Cond. 12 AWG Strd. Unshielded CL2P | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 12 | 19x25 | Bare | Plenum PVC | 0.012 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.263 in. | BK, GY | 150 V | 0 to 75 C | NFPA 262 Plenum | CL2P | Yes | 146 lbs | 2.367 in | 54 lbs | 1.7 Ohms/1000 Ft. | 36 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C12PBK 2/12 Unshielded CL2P Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C14P | 2 Cond. 14 AWG Strd. Unshielded CL2P | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 14 | 19x27 | Bare | Plenum PVC | 0.012 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.223 in. | BK, GY, GN, WH | 150 V | 0 to 75 C | NFPA 262 Plenum | CL2P | Yes | 84 lbs | 2.007 in | 36 lbs | 2.7 Ohms/1000 Ft. | 36 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C14PBK 2/14 Unshielded CL2P Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C16P | 2 Cond. 16 AWG Strd. Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 16 | 19x29 | Bare | Plenum PVC | 0.008 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.176 in. | BK, GY, GN, SGN, WH | 300 V | 0 to 75 C | NFPA 262 Plenum | CMP | Yes | 54 lbs | 1.583 in | 25 lbs | 4.2 Ohms/1000 Ft. | 36.5 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C16PBK 2/16 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C16PS | 2 Cond. 16 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 16 | 19x29 | Bare | Plenum PVC | 0.008 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.178 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 69 lbs | 1.60 in. | 30 lbs | 4.2 Ohms/1000 Ft. | 75 pf/ft | 140 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C16PSBK 2/16 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C18P | 2 Cond. 18 AWG Strd. Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 18 | 7x26 | Bare | Plenum PVC | 0.008 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.154 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 42 lbs | 1.386 in. | 17 lbs | 6.2 Ohms/1000 Ft. | 68 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C18PBK 2/18 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C18PS | 2 Cond. 18 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 18 | 7x26 | Bare | Plenum PVC | 0.008 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.156 in. | BK, YE, GY, WH | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 57 lbs | 1.404 in. | 21 lbs | 6.2 Ohms/1000 Ft. | 68 pf/ft | 122 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C18PSBK 2/18 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C20PS | 2 Cond. 20 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 20 | 7x28 | Bare | Plenum PVC | 0.008 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.138 in. | BK, YE | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 39 lbs | 1.242 in. | 15 lbs | 10.5 Ohms/1000 Ft. | 60 pf/ft | 108 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C20PSBK 2/20 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C20P | 2 Cond. 20 AWG Strd. Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 20 | 7x28 | Bare | Plenum PVC | 0.008 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.134 in. | BK | 300 V | 0 to 75 C | NFPA 262 Plenum | CMP | Yes | 26 lbs | 1.206 in. | 13 lbs | 10.5 Ohms/1000 Ft. | 30 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C20PBK 2/20 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C22P | 2 Cond. 22 AWG Strd. Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 22 | 7x30 | Bare | Plenum PVC | 0.007 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.116 in. | BK | 300 V | 0 to 75 C | NFPA 262 Plenum | CMP | Yes | 18 lbs | 1.004 in. | 10 lbs | 17 Ohms/1000 Ft. | 55 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C22PBK 2/22 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2C22PS | 2 Cond. 22 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 22 | 7x30 | Bare | Plenum PVC | 0.007 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.116 in. | BK, WH, GY | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 28 lbs | 1.044 in. | 11 lbs | 17.5 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C22PSBK 2/22 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2CS22SP | 2 Cond. 22 AWG Solid Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 2 | 22 | Solid | Bare | Plenum PVC | 0.008 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.116 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 28 lbs | 1.044 in. | 11 lbs | 17.5 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2C22SPSBK 2/22 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2P22PIS | 2 Pair 22 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 22 | 7x30 | Bare | Plenum PVC | 0.007 in. | BK & RD, WH & GN | Individually Shielded Pairs | Tinned Copper | Plenum PVC | 0.015 in. | 0.195 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 46 lbs | 1.75 in. | 22 lbs | 17 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2P22PBK 4/22 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
2P18PIS | 2 Pair 18 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 18 | 7x26 | Bare | Plenum PVC | 0.008 in. | BK & RD, WH & GN | Individually Shielded Pairs | Tinned Copper | Plenum PVC | 0.015 in. | 0.253 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 95 lbs | 2.277 in. | 43 lbs | 6.2 Ohms/1000 Ft. | 68 pf/ft | 122 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #2PS18BK 4/18 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
3C18P | 3 Cond. 18 AWG Strd. Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 3 | 18 | 7x26 | Bare | Plenum PVC | 0.008 in. | BK, RD, WH | N/A | N/A | Plenum PVC | 0.015 in. | 0.162 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 66 lbs | 1.458 in. | 25 lbs | 6.2 Ohms/1000 Ft. | 34 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #3C18PBK 3/18 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
3C18PS | 3 Cond. 18 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 3 | 18 | 7x26 | Bare | Plenum PVC | 0.008 in. | BK, RD, WH | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.166 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 66 lbs | 1.494 in. | 29 lbs | 6.2 Ohms/1000 Ft. | 68 pf/ft | 122 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #3C18PSBK 3/18 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
3C22PS | 3 Cond. 22 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 3 | 22 | 7x30 | Bare | Plenum PVC | 0.007 in. | BK, RD, WH | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.130 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 30 lbs | 1.17 in. | 18 lbs | 17 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #3C22PSBK 3/22 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
4C12P | 4 Cond. 12 AWG Strd. Unshielded CL2P | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 12 | 19x25 | Bare | Plenum PVC | 0.012 in. | BK, RD, WH, GN | N/A | N/A | Plenum PVC | 0.015 in. | 0.308 in. | BK | 150 V | 0 to 60 C | NFPA 262 Plenum | CL2P | Yes | 250 lbs | 2.772 in. | 104 lbs | 1.7 Ohms/1000 Ft. | 39 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #4C12PBK 4/12 Unshielded CL2P Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
4C16P | 4 Cond. 16 AWG Strd. Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 16 | 19x29 | Bare | Plenum PVC | 0.008 in. | BK, RD, WH, GN | N/A | N/A | Plenum PVC | 0.015 in. | 0.208 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 92 lbs | 1.87 in. | 44 lbs | 4.2 Ohms/1000 Ft. | 36.5 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #4C16PBK 4/16 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
4C18P | 4 Cond. 18 AWG Strd. Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 18 | 7x26 | Bare | Plenum PVC | 0.008 in. | BK, RD, WH, GN | N/A | N/A | Plenum PVC | 0.015 in. | 0.180 in. | BK, WH | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 80 lbs | 1.61 in. | 32 lbs | 6.2 Ohms/1000 Ft. | 68 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #4C18PBK 4/18 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
4C18PS | 4 Cond. 18 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 18 | 7x26 | Bare | Plenum PVC | 0.008 in. | BK, RD, WH, GN | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.182 in. | BK, WH | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 95 lbs | 1.638 in. | 36 lbs | 6.2 Ohms/1000 Ft. | 68 pf/ft | 122 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #4C18PSBK 4/18 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
4C20P | 4 Cond. 20 AWG Strd. Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 20 | 7x28 | Bare | Plenum PVC | 0.008 in. | BK, RD, WH, GN | N/A | N/A | Plenum PVC | 0.015 in. | 0.156 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 39 lbs | 1.404 in. | 22 lbs | 10.1 Ohms/1000 Ft. | 28.25 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #4C20PBK 4/20 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
4C22P | 4 Cond. 22 AWG Strd. Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 22 | 7x30 | Bare | Plenum PVC | 0.007 in. | BK, RD, WH, GN | N/A | N/A | Plenum PVC | 0.015 in. | 0.136 in. | BK, WH | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 29 lbs | 1.22 in. | 17 lbs | 16.1 Ohms/1000 Ft. | 27 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #4C22PBK 4/22 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
4C22PS | 4 Cond. 22 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 22 | 7x30 | Bare | Plenum PVC | 0.007 in. | BK, RD, WH, GN | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.141 in. | BK, WH | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 42 lbs | 1.269 in. | 18 lbs | 17 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #4C22PSWH 4/22 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
4CS22P | 4 Cond. 22 AWG Solid Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 4 | 22 | Solid | Bare | Plenum PVC | 0.008 in. | BK, RD, WH, GN | N/A | N/A | Plenum PVC | 0.015 in. | 0.136 in. | BK, WH | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 34 lbs | 1.206 in. | 17 lbs | 17.5 Ohms/1000 Ft. | 25 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #4C22SPBK 4/22 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
6C18PS | 6 Cond. 18 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 6 | 18 | 7x26 | Bare | Plenum PVC | 0.008 in. | BK, RD, WH, GN, BN, BL | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.221 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 140 lbs | 1.989 in. | 50 lbs | 6.2 Ohms/1000 Ft. | 60 pf/ft | 122 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #6C18PSBK 6/18 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
6C22P | 6 Cond. 22 AWG Strd. Unshielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 6 | 22 | 7x30 | Bare | Plenum PVC | 0.007 in. | BK, RD, WH, GN, BN, BL | N/A | N/A | Plenum PVC | 0.015 in. | 0.157 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 54 lbs | 1.413 in. | 25 lbs | 17 Ohms/1000 Ft. | 27 pf/ft | N/A | Audio, Control, Low Voltage Power | Provideon Wire & Cable #6C22PBK 6/22 Unshielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
6C22PS | 6 Cond. 22 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 6 | 22 | 7x30 | Bare | Plenum PVC | 0.007 in. | BK, RD, WH, GN, BN, BL | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.157 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 54 lbs | 1.413 in. | 25 lbs | 17 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #6C22PSBK 6/22 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
D1P22RIS | 2 Cond. 22 AWG Strd. Bonded Shield CM | Pro-Comm A/V/Pro Audio | 2 | 22 | 7x30 | Tinned | Polypropylene - PP | 0.008 in. | BK, RD | Bonded Overall 100% Aluminum Foil | Tinned Copper | PVC | 0.020 in. | 0.135 in. | BK | 300 V | `-20 to 60 C | UL 1666 Vertical Shaft | CM | Yes | 28 lbs | 1.215 in. | 15 lbs | 17 Ohms/1000 Ft. | 34 pf/ft | 67 pf/ft | Audio, Control, Low Voltage Power
L2CS16P | 2 Cond. 16 AWG Solid Unshielded CMP | LSS/LED | 2 | 16 | Solid | Bare | Plenum PVC | 0.008 in. | VT, PK | N/A | N/A | Plenum PVC | 0.014 in. | 0.164 in. | WH | 300 V | `-20 to 60 C | NFPA 262 Plenum | CMP | Yes | 54 lbs | 1.583 in. | 25 lbs | 4.2 Ohms/1000 Ft. |  | N/A | Audio, Control, Low Voltage Power
D2P24PTCS | 2 pair 24 (7X32) TINNED SHIELDED CMP RS-485 | LSS/RS 485 | 4 | 24 | Stranded | Tinned | Foam FEP | 0.023 in. | BL-WH, BL; OR-WH, OR | Overall 100% AL Foil, 90% Tinned Copper Braid | Tinned Copper | Plenum PVC | 0.017 in. | 0.305 in. | GY | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 56 lbs | 2.745 in. | 38 lbs | 26 Ohms/1000 Ft. | 12.8 pf/ft | 23 pf/ft | RS-485, DMX, Low Capacitance
D1P24PTCS | 1 pair 24 (7X32) TINNED SHIELDED CMP RS-485 | LSS/RS 485 | 2 | 24 | Stranded | Tinned | Foam FEP | 0.023 in. | BL-WH, BL | Overall 100% AL Foil, 90% Tinned Copper Braid | Tinned Copper | Plenum PVC | 0.017 in. | 0.202 in. | GY | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 45 lbs | 1.818 in. | 27 lbs | 26 Ohms/1000 Ft. | 12.8 pf/ft | 23 pf/ft | RS-485, DMX, Low Capacitance
D1P22PIS | 1 PR 22 (7x30) Tinned SHLD CMP, FEP Ins, PVC Jacket | Pro-Comm A/V/Pro Audio | 2 | 22 | 7x30 | Tinned | FEP | 0.007 in. | BK, RD | Bonded Overall 100% Aluminum Foil | Tinned Copper
3P22PS | 6 Cond. (3 Pair) 22 AWG Strd. Shielded CMP | Pro-Comm A/V/Commercial Audio and LV Comm. + Control/Comm. + Control | 6 | 22 | 7x30 | Bare | Plenum PVC | 0.007 in. | BK, RD, WH, GN, BN, BL | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.157 in. | BK | 300 V | 0 to 60 C | NFPA 262 Plenum | CMP | Yes | 54 lbs | 1.413 in. | 25 lbs | 17 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Audio, Control, Low Voltage Power | Provideon Wire & Cable #3P22PSBK 6/22 Shielded CMP Audio Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code

## Conductored Template
2C10P
Cable Description | 2 Cond. 10 AWG Strd. Unshielded CL2P
Cable Use Applications | Audio, Control, Low Voltage Power
Conductor Characteristics
Number of Conductors | 2
Gauge Size | 10
Stranding | 68x28
Conductor Type | Bare
Nominal Resistance | 1.1 Ohms/1000ft.
Insulation Type | Plenum PVC
Insulation Thickness | 0.012 in.
Insulation Color Code | BK, WH
Shielding Characteristics
Shielding | N/A
Shielding Drain | N/A
Nominal Capacitance - Conductor to Conductor | 28 pf/ft
Nominal Capacitance - Conductor to Shield | N/A
Jacket
Jacket Type | Plenum PVC
Jacket Thickness | 0.015 in.
Product Characteristics
Overall Diameter | 0.275 in.
Standard Jacket Color | BK
Voltage Rating | 150 V
Operating Temperature | 0 to 60 C
Flame Test | NFPA 262 Plenum
NEC Rating | CL2P
RoHS Compliant | Yes
Max Pull Tension | 260 lbs
Max Bend Radius | 2.75 in.
Cable Weight | 88 lbs

## Fire Alarm
Part Number | Description | Cable Type | # of Condctors | AWG Size | Stranding | Copper Type | Insulation | Insulation Thickness | Insulation color Code | Shielding | Drain Wire Type | Jacket Type | Jacket Thickness | Nominal Cable O.D. | Jacket Colors | Voltage Rating | Operating Temperature | Flame Test | NEC Rating | RoHS Compliant | Max Pull Tension | Max Bend Radius | Cable Weight | Nominal DCR | Nom. Cap. Between Cond. | Nom. Cap. Cond. To Shield | Applications | Cable Print
DF1P14RS | 2 Cond. 14 AWG Solid Shielded FPLR | LSS/Fire Alarm/Digital | 2 | 14 | Solid | Bare | Polypropylene - PP | 0.015 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | PVC | 0.030 in. | 0.281 in. | RD | 300 V | `-20 to 60C | UL 1666 Vertical Shaft | FPLR | Yes | 99 lbs | 2.529 in. | 47 lbs | 2.6 Ohms/1000 ft. | 30 pf/ft | 54 pf/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #DF1P14RSRD 2/14 Shielded FPLR Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DF1P16R | 2 Cond. 16 AWG Solid Unshielded FPLR | LSS/Fire Alarm/Digital | 2 | 16 | Solid | Bare | Polypropylene - PP | 0.015 in. | BK, RD | N/A | N/A | PVC | 0.030 in. | 0.223 in. | RD | 300 V | `-20 to 75C | UL 1666 Vertical Shaft | FPLR | Yes | 62 lbs | 2.007 in. | 29 lbs | 4.1 Ohms/1000 Ft. | 17 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #DF1P16RRD 2/16 Unshielded FPLR Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DF1P16RS | 2 Cond. 16 AWG Solid Shielded FPLR | LSS/Fire Alarm/Digital | 2 | 16 | Solid | Bare | Polypropylene - PP | 0.015 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | PVC | 0.030 in. | 0.245 in. | RD | 300 V | `-20 to 75C | UL 1666 Vertical Shaft | FPLR | Yes | 76 lbs | 2.205 in. | 34 lbs | 4.1 Ohms/1000 Ft. | 30 pf/ft | 54 pf/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #DF1P16RSRD 2/16 Shielded FPLR Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DF1P18R | 2 Cond. 18 AWG Solid Unshielded FPLR | LSS/Fire Alarm/Digital | 2 | 18 | Solid | Bare | Polypropylene - PP | 0.015 in. | BK, RD | N/A | N/A | PVC | 0.030 in. | 0.196 in. | RD | 300 V | `-20 to 75C | UL 1666 Vertical Shaft | FPLR | Yes | 39 lbs | 1.764 in. | 22 lbs | 6.5 Ohms/1000 Ft. | 15 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #DF1P18RRD 2/16 Unshielded FPLR Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DF1P18RS | 2 Cond. 18 AWG Solid Shielded FPLR | LSS/Fire Alarm/Digital | 2 | 18 | Solid | Bare | Polypropylene - PP | 0.015 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | PVC | 0.030 in. | 0.223 in. | RD | 300 V | `-20 to 75C | UL 1666 Vertical Shaft | FPLR | Yes | 43 lbs | 2.007 in. | 27 lbs | 6.5 Ohms/1000 Ft. | 25 pf/ft | 45 pf/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #DF1P18RSRD 2/18 Shielded FPLR Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DF1P18PS | 2 COND 18 SOLID BARE SHIELDED FPLP, FEP Ins., PVC Jacket | LSS/Fire Alarm/Digital |  | 18 | Solid | Bare | FEP | 0.012 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.165 in. | RD | 300 V | `-20 to 75C | NFPA 262 Plenum | FPLP | Yes | 53 lbs | 1.485 in. | 27 lbs | 6.5 Ohms/1000 Ft. | 25 pf/ft | 45 pf/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.24
DF2C18P | 2 COND 18 SOLID BARE FPLP, FEP Ins , PVC Jacket | LSS/Fire Alarm/Digital |  | 18 | Solid | Bare | FEP | 0.012 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.160 in. | RD | 300 V | `-20 to 75C | NFPA 262 Plenum | FPLP | Yes | 53 lbs | 1.296 in. | 19 lbs | 6.5 Ohms/1000 Ft. | 16 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.25
DF1P16P | 2 COND 16 SOLID BARE FPLP, FEP Ins., PVC Jacket | LSS/Fire Alarm/Digital |  | 16 | Solid | Bare | FEP | 0.012 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.181 in. | RD | 300 V | `-20 to 75C | NFPA 262 Plenum | FPLP | Yes | 62 lbs | 1.476 in. | 22 lbs | 4.1 Ohms/1000 Ft. | 16 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.26
DF1P16PS | 2 COND 16 SOLID BARE SHIELDED FPLP, FEP Ins., PVC Jacket | LSS/Fire Alarm/Digital |  | 16 | Solid | Bare | FEP | 0.012 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.188 in. | RD | 300 V | `-20 to 75C | NFPA 262 Plenum | FPLP | Yes | 74 lbs | 1.692 in. | 35 lbs | 4.1 Ohms/1000 Ft. | 30 pf/ft | 54 pf/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.27
F1P12P | 2 Cond. 12 AWG Solid Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 12 | Solid | Bare | Plenum PVC | 0.009 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.239 in. | RD | 300 V | `-20 to 75C | NFPA 262 Plenum | FPLP | Yes | 159 lbs | 2.151 in. | 55 lbs | 1.8 Ohm/1000 Ft. | 40 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P12PRD 2/12 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1P12SP | 2 Cond. 12 AWG Solid Shielded FPLP | LSS/Fire Alarm/Analog | 2 | 12 | Solid | Bare | Plenum PVC | 0.009 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.239 in. | RD | 300 V | `-20 to 75C | NFPA 262 Plenum | FPLP | Yes | 159 lbs | 2.151 in. | 55 lbs | 1.8 Ohm/1000 Ft. | 84 pF/ft | 151 pF/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P12SPRD 2/12 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1P14P | 2 Cond. 14 AWG Solid Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 14 | Solid | Bare | Plenum PVC | 0.009 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.198 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 99 lbs | 1.476 in. | 36 lbs | 2.6 Ohms/1000 ft. | 34 pF/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P14PRD 2/14 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1P14PS | 2 Cond. 14 AWG Solid Shielded FPLP | LSS/Fire Alarm/Analog | 2 | 14 | Solid | Bare | Plenum PVC | 0.009 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.202 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 113 lbs | 1.818 in. | 39 lbs | 2.6 Ohms/1000 ft. | 84 pF/ft | 151 pF/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P14PSRD 2/14 Shielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1PS14P | 2 Cond. 14 AWG Strd. Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 14 | 19x27 | Bare | Plenum PVC | 0.010 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.198 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 99 lbs | 1.782 in. | 36 lbs | 2.6 Ohms/1000 ft. | 34 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P14SPSTWH 2/14 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1PS14P | 2 Cond. 14 AWG Strd. Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 14 | 19x27 | Bare | Plenum PVC | 0.010 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.198 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 99 lbs | 1.782 in. | 36 lbs | 2.6 Ohms/1000 ft. | 34 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P14SPSTYE 2/14 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1P14P | 2 Cond. 14 AWG Solid Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 14 | Solid | Bare | Plenum PVC | 0.009 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.198 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 99 lbs | 1.476 in. | 36 lbs | 2.6 Ohms/1000 ft. | 34 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P14PTBK 2/14 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1PS14P | 2 Cond. 14 AWG Strd. Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 14 | 19x27 | Bare | Plenum PVC | 0.009 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.198 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 99 lbs | 1.782 in. | 36 lbs | 2.6 Ohms/1000 ft. | 34 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P14SPRD 2/14 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1PS14PS | 2 Cond. 14 AWG Strd. Shielded FPLP | LSS/Fire Alarm/Analog | 2 | 14 | 19x27 | Bare | Plenum PVC | 0.009 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.202 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 113 lbs | 1.818 in. | 39 lbs | 2.6 Ohms/1000 ft. | 84 pF/ft | 151 pF/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P14SPSRD 2/14 Shielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1P16P | 2 Cond. 16 AWG Solid Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 16 | Solid | Bare | Plenum PVC | 0.008 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.164 in. | RD | 300 V | 0 to 60 C | NFPA 262 Plenum | FPLP | Yes | 62 lbs | 1.476 in. | 26 lbs | 4.1 Ohms/1000 Ft. | 33 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P16PRD 2/16 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1P16PS | 2 Cond. 16 AWG Solid Shielded FPLP | LSS/Fire Alarm/Analog | 2 | 16 | Solid | Bare | Plenum PVC | 0.008 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.168 in. | RD | 300 V | 0 to 60 C | NFPA 262 Plenum | FPLP | Yes | 76 lbs | 1.512 in. | 29 lbs | 4.1 Ohms/1000 Ft. | 77 pf/ft | 139 pf/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P16PSRD 2/16 Shielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1P16P | 2 Cond. 16 AWG Solid Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 16 | Solid | Bare | Plenum PVC | 0.008 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.164 in. | WH | 300 V | 0 to 60 C | NFPA 262 Plenum | FPLP | Yes | 62 lbs | 1.476 in. | 26 lbs | 4.1 Ohms/1000 Ft. | 33 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P16PWH 2/16 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1PS16P | 2 Cond. 16 AWG Strd. Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 16 | 19x29 | Bare | Plenum PVC | 0.008 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.164 in. | RD | 300 V | 0 to 60 C | NFPA 262 Plenum | FPLP | Yes | 76 lbs | 1.476 in. | 26 lbs | 4.1 Ohms/1000 Ft. | 33 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P16SPRD 2/16 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1PS16PS | 2 Cond. 16 AWG Strd. Shielded FPLP | LSS/Fire Alarm/Analog | 2 | 16 | 19x29 | Bare | Plenum PVC | 0.008 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.168 in. | RD | 300 V | 0 to 60 C | NFPA 262 Plenum | FPLP | Yes | 76 lbs | 1.494 in. | 29 lbs | 4.1 Ohms/1000 Ft. | 77 pf/ft | 139 pf/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P16SPSRD 2/16 Shielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1P18PS | 2 Cond. 18 AWG Solid Shielded FPLP | LSS/Fire Alarm/Analog | 2 | 18 | Solid | Bare | Plenum PVC | 0.008 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.148 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 53 lbs | 1.33 in. | 22 lbs | 6.5 Ohms/1000 Ft. | 66 pf/ft | 119 pf/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P18PSRD 2/18 Shielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1PS18PS | 2 Cond. 18 AWG Strd. Shielded FPLP | LSS/Fire Alarm/Analog | 2 | 18 | 7x26 | Bare | Plenum PVC | 0.008 in. | BK, RD | Overall 100% AL Foil | Tinned Copper | Plenum PVC | 0.015 in. | 0.148 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 53 lbs | 1.33 in. | 22 lbs | 6.5 Ohms/1000 Ft. | 66 pf/ft | 119 pf/ft | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.24 | Provideon Wire & Cable #F1P18SPSRD 2/18 Shielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1P18P | 2 Cond. 18 AWG Solid Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 18 | Solid | Bare | Plenum PVC | 0.008 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.144 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 32 lbs | 1.33 in. | 18 lbs | 6.5 Ohms/1000 Ft. | 31 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F1P18PRD 2/18 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F1PS18P | 2 Cond. 18 AWG Strd. Unshielded FPLP | LSS/Fire Alarm/Analog | 2 | 18 | 7x26 | Bare | Plenum PVC | 0.008 in. | BK, RD | N/A | N/A | Plenum PVC | 0.015 in. | 0.145 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 53 lbs | 1.29 in. | 19 lbs | 6.5 Ohms/1000 Ft. | 31 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.24 | Provideon Wire & Cable #F1P18SPRD 2/18 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
F4C18P | 4 Cond. 18 AWG Solid Unshielded FPLP | LSS/Fire Alarm/Analog | 4 | 18 | Solid | Bare | Plenum PVC | 0.008 in. | BK, RD, BN, BL | N/A | N/A | Plenum PVC | 0.015 in. | 0.166 in. | RD | 300 V | 0 to 75 C | NFPA 262 Plenum | FPLP | Yes | 84 lbs | 1.494 in. | 32 lbs | 6.5 Ohms/1000 Ft. | 31 pf/ft | N/A | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23 | Provideon Wire & Cable #F4C18PRD 4/18 Unshielded FPLP Fire Alarm Cable A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code

## Fire Alarm Template
DF1P14RS
Cable Description | 2 Cond. 14 AWG Solid Shielded FPLR
Cable Use Applications | Fire Alarm, Initiating Devices, Notification Devices, Div. 28 05 13.23
Conductor Characteristics
Number of Conductors | 2
Gauge Size | 14
Stranding | Solid
Conductor Type | Bare
Nominal Resistance | 2.6 Ohms/1000 ft.
Insulation Type | Polypropylene - PP
Insulation Thickness | 0.015 in.
Insulation Color Code | BK, RD
Shielding Characteristics
Shielding | Overall 100% AL Foil
Shielding Drain | Tinned Copper
Nominal Capacitance - Conductor to Conductor | 30 pf/ft
Nominal Capacitance - Conductor to Shield | 54 pf/ft
Jacket
Jacket Type | PVC
Jacket Thickness | 0.030 in.
Product Characteristics
Overall Diameter | 0.281 in.
Standard Jacket Color | RD
Voltage Rating | 300 V
Operating Temperature | `-20 to 60C
Flame Test | UL 1666 Vertical Shaft
NEC Rating | FPLR
RoHS Compliant | Yes
Max Pull Tension | 99 lbs
Max Bend Radius | 2.529 in.
Cable Weight | 47 lbs

## Water Otter
Part Number | Description | Cable Type | # of Condctors | AWG Size | Stranding | Copper Type | Insulation | Insulation Thickness | Insulation color Code | Shielding | Drain Wire Type | Jacket Type | Jacket Thickness | Nominal Cable O.D. | Jacket Colors | Voltage Rating | Operating Temperature | Flame Test | NEC Rating | RoHS Compliant | Max Pull Tension | Max Bend Radius | Cable Weight | Nominal DCR | Nom. Cap. Between Cond. | Nom. Cap. Cond. To Shield | Applications | Cable Print
DB2C18 | 2 Cond. 18 AWG Strd. Unshielded WO | Water Otter/Direct Burial | 2 | 18 | 7x26 | Bare | PVC/Nylon | 0.020 in. | BK, RD | WO Tape | N/A | UV Resistant PVC | 0.040 in. | 0.270 in. | BK | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL, PLTC | Yes | 54 lbs | 2.43 in. | 39 lbs | 6.2 Ohms/1000 Ft. | 25 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #DB2C18BK 2/18 Unshielded FPL CL3 PLTC Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DB2C16 | 2 Cond. 16 AWG Strd. Unshielded WO | Water Otter/Direct Burial | 2 | 16 | 19x29 | Bare | PVC/Nylon | 0.020 in. | BK, RD | WO Tape | N/A | UV Resistant PVC | 0.040 in. | 0.295 in. | BK | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL, PLTC | Yes | 55 lbs | 2.655 in. | 48 lbs | 4.2 Ohms/1000 Ft. | 28 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #DB2C16BK 2/16 Unshielded FPL CL3 PLTC Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DB2C14 | 2 Cond. 14 AWG Strd. Unshielded WO | Water Otter/Direct Burial | 2 | 14 | 19x27 | Bare | PVC/Nylon | 0.020 in. | BK, RD | WO Tape | N/A | UV Resistant PVC | 0.040 in. | 0.310 in. | BK | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL, PLTC | Yes | 84 lbs | 2.79 in. | 59 lbs | 2.7 Ohms/1000 Ft. | 32 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #DB2C14BK 2/14 Unshielded FPL CL3 PLTC Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DB2C12 | 2 Cond. 12 AWG Strd. Unshielded WO | Water Otter/Direct Burial | 2 | 12 | 19x25 | Bare | PVC/Nylon | 0.020 in. | BK, RD | WO Tape | N/A | UV Resistant PVC | 0.040 in. | 0.340 in. | BK | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL, PLTC | Yes | 146 lbs | 3.06 in. | 78 lbs | 1.7 Ohms/1000 Ft. | 32 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #DB2C12BK 2/12 Unshielded FPL CL3 PLTC Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DB4C18 | 4 Cond. 18 AWG Strd. Unshielded WO | Water Otter/Direct Burial | 4 | 18 | 7x26 | Bare | PVC/Nylon | 0.020 in. | BK, RD, BN, BL | WO Tape | N/A | UV Resistant PVC | 0.040 in. | 0.327 in. | BK | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL, PLTC | Yes | 98 lbs | 2.943 in. | 56 lbs | 6.2 Ohms/1000 Ft. | 25 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #DB4C18BK 4/18 Unshielded FPL CL3 PLTC Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DB4C16 | 4 Cond. 16 AWG Strd. Unshielded WO | Water Otter/Direct Burial | 4 | 16 | 19x29 | Bare | PVC/Nylon | 0.020 in. | BK, RD, BN, BL | WO Tape | N/A | UV Resistant PVC | 0.040 in. | 0.355 in. | BK | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL, PLTC | Yes | 108 lbs | 3.195 in. | 75 lbs | 4.2 Ohms/1000 Ft. | 28 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #DB4C18BK 4/16 Unshielded FPL CL3 PLTC Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DB2C18S | 2 Cond. 18 AWG Strd. Shielded WO | Water Otter/Direct Burial | 2 | 18 | 7x26 | Bare | PVC/Nylon | 0.020 in. | BK, RD | WO Tape, Overall 100% AL Foil | Tinned Copper | UV Resistant PVC | 0.040 in. | 0.310 in. | BK | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL, PLTC | Yes | 57 lbs | 2.79 in. | 49 lbs | 6.2 Ohms/1000 Ft. | 32 pf/ft | 58 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #DB2C18SBK 2/18 Shielded FPL CL3 PLTC Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DB2C16S | 2 Cond. 16 AWG Strd. Shielded WO | Water Otter/Direct Burial | 2 | 16 | 19x29 | Bare | PVC/Nylon | 0.020 in. | BK, RD | WO Tape, Overall 100% AL Foil | Tinned Copper | UV Resistant PVC | 0.040 in. | 0.328 in. | BK | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL, PLTC | Yes | 69 lbs | 2.952 in. | 58 lbs | 4.2 Ohms/1000 Ft. | 37 pf/ft | 67 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #DB2C16SBK 2/16 Shielded FPL CL3 PLTC Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DB2C14S | 2 Cond. 14 AWG Strd. Shielded WO | Water Otter/Direct Burial | 2 | 14 | 19x27 | Bare | PVC/Nylon | 0.020 in. | BK, RD | WO Tape, Overall 100% AL Foil | Tinned Copper | UV Resistant PVC | 0.040 in. | 0.350 in. | BK | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL, PLTC | Yes | 99 lbs | 3.15 in. | 67 lbs | 2.7 Ohms/1000 Ft. | 46 pf/ft | 83 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #DB2C14SBK 2/14 Shielded FPL CL3 PLTC Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
DB4C18S | 4 Cond. 18 AWG Strd. Shielded WO | Water Otter/Direct Burial | 4 | 18 | 7x26 | Bare | PVC/Nylon | 0.020 in. | BK, RD, BN, BL | WO Tape, Overall 100% AL Foil | Tinned Copper | UV Resistant PVC | 0.040 in. | 0.371 in. | BK | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL, PLTC | Yes | 72 lbs | 3.339 in. | 60 lbs | 6.2 Ohms/1000 Ft. | 32 pf/ft | 58 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #DB4C18SBK 4/18 Shielded FPL CL3 PLTC Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2C18 | 2 Cond. 18 AWG Strd. Unshielded WO | Water Otter/Indoor/Outdoor | 2 | 18 | 7x26 | Bare | PVC | 0.010 in. | BK, RD | WO Tape | N/A | UV Resistant PVC | 0.025 in. | 0.218 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3, FPL | Yes | 43 lbs | 1.962 in. | 26 lbs | 6.2 Ohms/1000 Ft. | 30 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2C18GY 2/18 Unshielded FPL CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2C16 | 2 Cond. 16 AWG Strd. Unshielded WO | Water Otter/Indoor/Outdoor | 2 | 16 | 19x29 | Bare | PVC | 0.010 in. | BK, RD | WO Tape | N/A | UV Resistant PVC | 0.025 in. | 0.242 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3, FPL | Yes | 55 lbs | 2.178 in. | 29 lbs | 4.2 Ohms/1000 Ft. | 34 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2C16GY 2/16 Unshielded FPL CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2C14 | 2 Cond. 14 AWG Strd. Unshielded WO | Water Otter/Indoor/Outdoor | 2 | 14 | 19x27 | Bare | PVC | 0.010 in. | BK, RD | WO Tape | N/A | UV Resistant PVC | 0.025 in. | 0.294 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL | Yes | 82 lbs | 2.646 in. | 48 lbs | 2.7 Ohms/1000 Ft. | 34 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2C14GY 2/14 Unshielded FPL CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2C12 | 2 Cond. 12 AWG Strd. Unshielded WO | Water Otter/Indoor/Outdoor | 2 | 12 | 19x25 | Bare | PVC | 0.010 in. | BK, RD | WO Tape | N/A | UV Resistant PVC | 0.025 in. | 0.316 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CL3, FPL | Yes | 146 lbs | 3.06 in. | 68 lbs | 1.7 Ohms/1000 Ft. | 34 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2C12GY 2/12 Unshielded FPL CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB4CS22 | 4 Cond. 22 AWG Solid Unshielded WO | Water Otter/Indoor/Outdoor | 4 | 22 | Solid | Bare | PVC | 0.008 in. | BK, RD, WH, GN | WO Tape | N/A | UV Resistant PVC | 0.025 in. | 0.194 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3 | Yes | 50 lbs | 1.862 in. | 43 lbs | 17.5 Ohms/1000 Ft. | 25 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB4CS22SGY 4/22 Unshielded CM CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB4C18 | 4 Cond. 18 AWG Strd. Unshielded WO | Water Otter/Indoor/Outdoor | 4 | 18 | 7x26 | Bare | PVC | 0.010 in. | BK, RD, WH, GN | WO Tape | N/A | UV Resistant PVC | 0.025 in. | 0.245 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3, FPL | Yes | 91 lbs | 1.962 in. | 36 lbs | 6.2 Ohms/1000 Ft. | 30 pf/ft | N/A | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB4C18GY 4/18 Unshielded FPL CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2C22S | 2 Cond. 22 AWG Strd. Shielded WO | Water Otter/Indoor/Outdoor | 2 | 22 | 7x30 | Bare | PVC | 0.010 in. | BK, RD | WO Tape, Overall 100% AL Foil | Tinned Copper | UV Resistant PVC | 0.025 in. | 0.205 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3 | Yes | 33 lbs | 1.845 in. | 21 lbs | 17 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2C22SGY 2/22 Shielded CM CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2C20S | 2 Cond. 20 AWG Strd. Shielded WO | Water Otter/Indoor/Outdoor | 2 | 20 | 7x28 | Bare | PVC | 0.010 in. | BK, RD | WO Tape, Overall 100% AL Foil | Tinned Copper | UV Resistant PVC | 0.025 in. | 0.220 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3 | Yes | 39 lbs | 1.98 in. | 22 lbs | 10.5 Ohms/1000 Ft. | 60 pf/ft | 108 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2C20SGY 2/20 Shielded CM CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2C18S | 2 Cond. 18 AWG Strd. Shielded WO | Water Otter/Indoor/Outdoor | 2 | 18 | 7x26 | Bare | PVC | 0.010 in. | BK, RD | WO Tape, Overall 100% AL Foil | Tinned Copper | UV Resistant PVC | 0.025 in. | 0.257 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3, FPL | Yes | 57 lbs | 2.313 in. | 30 lbs | 6.2 Ohms/1000 Ft. | 68 pf/ft | 122 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2C18SGY 2/18 Shielded CM FPL CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2C16S | 2 Cond. 16 AWG Strd. Shielded WO | Water Otter/Indoor/Outdoor | 2 | 16 | 19x29 | Bare | PVC | 0.010 in. | BK, RD | WO Tape, Overall 100% AL Foil | Tinned Copper | UV Resistant PVC | 0.025 in. | 0.281 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3, FPL | Yes | 67 lbs | 2.529 in. | 34 lbs | 4.2 Ohms/1000 Ft. | 78 pf/ft | 138 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2C16SGY 2/16 Shielded CM FPL CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB6C18S | 6 Cond. 18 AWG Strd. Shielded WO | Water Otter/Indoor/Outdoor | 6 | 18 | 7x26 | Bare | PVC | 0.010 in. | BK, RD, WH, GN, BN, BL | WO Tape, Overall 100% AL Foil | Tinned Copper | UV Resistant PVC | 0.025 in. | 0.323 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3, FPL | Yes | 93 lbs | 2.907 in. | 54 lbs | 6.2 Ohms/1000 Ft. | 68 pf/ft | 122 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB6C18SGY 6/18 Shielded CM FPL CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB6C22S | 6 Cond. 22 AWG Strd. Shielded WO | Water Otter/Indoor/Outdoor | 6 | 22 | 7x30 | Bare | PVC | 0.010 in. | BK, RD, WH, GN, BN, BL | WO Tape, Overall 100% AL Foil | Tinned Copper | UV Resistant PVC | 0.025 in. | 0.220 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3 | Yes | 63 lbs | 1.503 in. | 29 lbs | 17 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB6C22SGY 6/22 Shielded CM CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2C1P22S | 4 Cond. 22 AWG Strd. Shielded WO | Water Otter/Indoor/Outdoor | 4 | 22 | 7x30 | Bare | PVC | 0.010 in. | (BK, RD Shld) WH, GN | WO Tape, 2 SH / 2 UNSH | Tinned Copper | UV Resistant PVC | 0.025 in. | 0.235 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3 | Yes | 51 lbs | 2.120 in. | 21 lbs | 17 Ohms/1000 Ft. | 54 pf/ft | 97 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2C1P22SGY 4/22 Shielded CM CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2C1P20S | 4 Cond. 20 AWG Strd. Shielded WO | Water Otter/Indoor/Outdoor | 4 | 20 | 7x28 | Bare | PVC | 0.010 in. | (BK, RD Shld) WH, GN | WO Tape, 2 SH / 2 UNSH | Tinned Copper | UV Resistant PVC | 0.025 in. | 0.266 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3 | Yes | 65 lbs | 2.394 in. | 28 lbs | 10.1 Ohms/1000 Ft. | 60 pf/ft | 108 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2C1P20SGY 4/20 Shielded CM CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code
WB2P22IS | 2 Pair 22 AWG Strd. Shielded WO | Water Otter/Indoor/Outdoor | 4 | 22 | 7x30 | Bare | PVC | 0.010 in. | BK & RD, WH & GN | WO Tape, Individually Shielded Pairs | Tinned Copper | UV Resistant PVC | 0.025 in. | 0.250 in. | GY | 300 V | `-20 to 90 C | UL 1685 | CM, CL3 | Yes | 60 lbs | 3.42 in. | 29 lbs | 17 Ohms/1000 Ft. | 55 pf/ft | 99 pf/ft | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm | Provideon Wire & Cable #WB2P22ISGY 4/22 Shielded CM CL3 Water Otter A B C D E F G H I J 1 2 3 4 5 6 7 8 9 0 Date Code

## Water Otter Template
DB2C12
Cable Description | 2 Cond. 12 AWG Strd. Unshielded WO
Cable Use Applications | Indoor & Outdoor Audio, Control, Low Voltage, Fire Alarm
Conductor Characteristics
Number of Conductors | 2
Gauge Size | 12
Stranding | 19x25
Conductor Type | Bare
Nominal Resistance | 1.7 Ohms/1000 Ft.
Insulation Type | PVC/Nylon
Insulation Thickness | 0.020 in.
Insulation Color Code | BK, RD
Shielding Characteristics
Shielding | WO Tape
Shielding Drain | N/A
Nominal Capacitance - Conductor to Conductor | 32 pf/ft
Nominal Capacitance - Conductor to Shield | N/A
Jacket
Jacket Type | UV Resistant PVC
Jacket Thickness | 0.040 in.
Product Characteristics
Overall Diameter | 0.340 in.
Standard Jacket Color | BK
Voltage Rating | 300 V
Operating Temperature | `-20 to 90 C
Flame Test | UL 1685
NEC Rating | CL3, FPL, PLTC
RoHS Compliant | Yes
Max Pull Tension | 146 lbs
Max Bend Radius | 3.06 in.
Cable Weight | 78 lbs

## Coax
Part Number | Description | Cable Type | # of Condctors | AWG Size | Stranding | Copper Type | Insulation (Coax) | Insulation Thickness (Coax) | Shield #1 | Shield #2 | Shield #3 | Shield #4 | Jacket Type | Nominal Cable O.D. | Jacket Colors | Voltage Rating | Operating Temperature | Flame Test | NEC Rating | RoHS Compliant | Max Pull Tension | Max Bend Radius | Cable Weight | Attenuation | Applications | Cable Print
C7518QAP | RG-6 18 SOLID CCS CATVP QUAD-SHIELD | Pro-Comm A/V/CATV | 1 | 18 | Solid | Copper Covered Steel | Foam FEP | 0.170 in. | Overall 100% AL Foil | 60% Aluminum Braid | 100% AL Foil | 40% Aluminum Braid | Plenum PVC | 0.270 in. | Ivory | 300 V | `-20 to 60 C | NFPA 262 | CMP | Yes | 85 lbs | 2.700 in. | 35 lbs | #VALUE! | CATV
C751895TP | RG-6 18 SOLID BARE CMP SDI COAX | Pro-Comm A/V/Pro Video | 1 | 18 | Solid | Bare Copper | Foam FEP | 0.170 in. | Overall 100% AL Foil | 95 % Tinned Copper Braid | N/A | N/A | Plenum PVC | 0.236 in. | Black | 300 V | `-20 to 60 C | NFPA 262 | CMP | Yes | 75 lbs | 2.36 in. | 36 lbs | #VALUE! | HD/SDI
C751895CP | RG-6 18 SOLID BARE CMP | LSS/CCTV | 1 | 18 | Solid | Bare Copper | Foam FEP | 0.170 in. | Overall 100% AL Foil | 95% Bare Copper Braid | N/A | N/A | Plenum PVC | 0.230 in. | Black | 300 V | `-20 to 60 C | NFPA 262 | CMP | Yes | 70 lbs | 2.30 in. | 36 lbs | #VALUE! | CCTV
C502095TP | RG-58 20 STND TIN 50 OHM PLENUM | Pro-Comm A/V/RF Trans | 1 | 20 | 19 x 32 | Tinned Copper | Foam FEP | 0.102 in. | Overall 100% AL Foil | 95% Tinned Copper Braid | N/A | N/A | Plenum PVC | 0.158 in. | Ivory | 300 V | `-20 to 60 C | NFPA 262 | CMP | Yes | 55 lbs | 1.580 in. | 24 lbs | #VALUE! | Wireless Microphone
C751855AP | RG-6 18 SOLID BARE CATVP | Pro-Comm A/V/CATV | 1 | 18 | Solid | Bare Copper | Foam FEP | 0.170 in. | Overall 100% AL Foil | 77% Aluminum Braid | N/A | N/A | Plenum PVC | 0.237 in. | Ivory | 300 V | `-20 to 60 C | NFPA 262 | CATVP, CMP | Yes | 70 lbs | 2.37 in. | 32 lbs | #VALUE! | CATV
C752X2095CP | RG-59 20 SOLID BARE CMP + 1 PAIR 18 STND SIAMESE | LSS/CCTV | 1 | 20 & 18 | Solid & Stranded | Bare Copper | Foam FEP | 0.138 in. | 95 % Bare Copper Braid | N/A | N/A | N/A | Plenum PVC | 0.198 x 0.465 in. | Black | 300 V | `-20 to 60 C | NFPA 262 | CMP | Yes | 75 lbs | 4.65 in. | 60 lbs | #VALUE! | CCTV
C751860AP | RG-6 18 SOLID CCS CATVP | Pro-Comm A/V/CATV | 1 | 18 | Solid | Copper Covered Steel | Foam FEP | 0.170 in. | Overall 100% AL Foil | 60% Aluminum Braid | N/A | N/A | Plenum PVC | 0.237 in. | Black | 300 V | `-20 to 60 C | NFPA 262 | CATVP, CMP | Yes | 70 lbs | 2.37 in. | 29 lbs | #VALUE! | CATV
C7518QAP | RG-6 18 SOLID CCS CATVP QUAD-SHIELD | Pro-Comm A/V/CATV | 1 | 18 | Solid | Copper Covered Steel | Foam FEP | 0.170 in. | Overall 100% AL Foil | 60% Aluminum Braid | 100% AL Foil | 40% Aluminum Braid | Plenum PVC | 0.270 in. | Black | 300 V | `-20 to 60 C | NFPA 262 | CMP | Yes | 85 lbs | 2.700 in. | 35 lbs | #VALUE! | CATV
C5016T | RG8/X Flexible 16Awg. BC 95% BC Braid 50 ohm Plenum | Pro-Comm A/V/RF Trans | 1 | 16 | Stranded | Bare Copper | Foam Polyethylene | 0.155 in. | Overall 100% AL Foil | 90% Tinned Copper | N/A | N/A | PVC | 0.242 in. | Black | 300 V | `-20 to 60 C | UL 1685 | CM | Yes | 85 lbs | 2.420 in. | 38 lbs | #VALUE! | Wireless Microphone
WBC751855Ap | RG-6 18 SOLID BARE CM AQUASEAL OUTDOOR | Pro-Comm A/V/CATV and Water Otter/Indoor/Outdoor | 1 | 18 | Solid | Bare Copper | Foam Polyethylene | 0.180 in. | Overall 100% AL Foil | 55% Aluminum Braid | N/A | N/A | UV Resistant PVC | 0.275 in. | Black | 300 V | `-20 to 60 C | UL 1685 | CM | Yes | 70 lbs | 2.75 in. | 36 lbs | #VALUE! | CATV
C755X26TCP | RGB/SYNC 5 MINIATURE 26 AWG CMP RATED FLEXIBLE | Pro-Comm A/V/Pro Video | 5 | 26 | 7 x 34 | Tinned Copper | Foam FEP | 0.073 in. | Overall 100% AL Foil | 95% Tinned Copper Braid | N/A | N/A | Plenum PVC | 0.108 in. / 0.310 in. | Black | 300 V | `-20 to 60 C | NFPA 262 | CMP | Yes | 65 lbs | 3.1 in. | 56 lbs | #VALUE! | Broadcast Video

## Coax Template
C7518QAP
Cable Description | RG-6 18 SOLID CCS CATVP QUAD-SHIELD
Cable Use Applications | CATV
Core Characteristics
Number of Conductors | 1
Gauge Size | 18
Stranding | Solid
Conductor Type | Copper Covered Steel
Insulation Type | Foam FEP
Insulation Thickness | 0.170 in.
Shielding Characteristics
Shield #1 | Overall 100% AL Foil
Shield #2 | 60% Aluminum Braid
Shield #3 | 100% AL Foil
Shield #4 | 40% Aluminum Braid
Product Characteristics
Jacket Type | Plenum PVC
Overall Diameter | 0.270 in.
Standard Jacket Color | Ivory
Voltage Rating | 300 V
Operating Temperature | `-20 to 60 C
Flame Test | NFPA 262
NEC Rating | CMP
RoHS Compliant | Yes
Max Pull Tension | 85 lbs
Max Bend Radius | 2.700 in.
Cable Weight | 35 lbs
#VALUE!
35 lbs
35 lbs
35 lbs
35 lbs
35 lbs
35 lbs
35 lbs
35 lbs
35 lbs
35 lbs
35 lbs
35 lbs
35 lbs

## Category Cables
Part Number | Description | Cable Type | # of Condctors | AWG Size | Stranding | Copper Type | Insulation | Insulation Thickness | Insulation color Code | Shielding | Drain Wire Type | Drain Wire AWG | Jacket Type | Nominal Cable O.D. | Jacket Colors | Voltage Rating | Operating Temperature | Flame Test | NEC Rating | RoHS Compliant | Max Pull Tension | Max Bend Radius | Cable Weight | Nominal DCR | Nom. Cap. Between Cond. | Nom. Cap. Cond. To Shield | Applications | Chart | Cable Print
N4P245EP | CATEGORY 5E CMP 4 PAIR | Networking/LAN | 8 | 24 AWG | Solid | Bare Copper | Flouropolymer | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | N/A | N/A | N/A | Plenum PVC | 0.191 in. | Black, Blue, Brown, Green, Gray, Orange, Pink, Security Green, Violet, White, Yellow | 300V | `-20 to 60 C | NFPA 262 | CMP | Yes | 25 lbs | 0.955 in. | 21 lbs | 26 Ohms/1000ft | 14 pF/ft | N/A | Networking, Security | #VALUE!
N4P236AP | CATEGORY 6A CMP 4 PAIR | Networking/LAN | 8 | 23 AWG | Solid | Bare Copper | Flouropolymer | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | N/A | N/A | N/A | Plenum PVC | 0.250 in. | Black, Blue, Pink, Yellow | 300V | `-20 to 60 C | NFPA 262 | CMP | Yes | 25 lbs | 1.250 in. | 37 lbs | 24 Ohms/1000ft | 13 pF/ft | N/A | Networking, Security | #VALUE!
N4P236APS | CATEGORY 6A CMP 4 PAIR SHIELDED | Networking/LAN | 8 | 23 AWG | Solid | Bare Copper | Flouropolymer | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | Overall Aluminum Foil | Tinned Copper | 24 AWG | Plenum PVC | 0.265 in. | Black, White | 300V | `-20 to 60 C | NFPA 262 | CMP | Yes | 25 lbs | 1.325 in. | 37 lbs | 24 Ohms/1000ft | 13 pF/ft | N/A | Networking, Security | #VALUE!
N4P236P | CATEGORY 6 CMP 4 PAIR | Networking/LAN | 8 | 23 AWG | Solid | Bare Copper | Flouropolymer | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | N/A | N/A | N/A | Plenum PVC | 0.225 in. | Black, Blue, Green, Gray, Orange, Pink, Security Green, Violet, White, Yellow | 300V | `-20 to 60 C | NFPA 262 | CMP | Yes | 40 lbs | 1.125 in. | 27 lbs | 24 Ohms/1000ft | 14 pF/ft | N/A | Networking, Security | #VALUE!
N4P236PS | CATEGORY 6 CMP 4 PAIR SHIELDED | Networking/LAN | 8 | 23 AWG | Solid | Bare Copper | Flouropolymer | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | Overall Aluminum Foil | Tinned Copper | 26 AWG | PVC | 0.255 in. | Black | 300V | `-20 to 60 C | NFPA 262 | CMP | Yes | 25 lbs | 1.105 in. | 37 lbs | 24 Ohms/1000ft | 13 pF/ft | N/A | Networking, Security | #VALUE!
N4P245E | CATEGORY 5E CMR 4 PAIR | Networking/LAN | 8 | 24 AWG | Solid | Bare Copper | Polyolefin | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | N/A | N/A | N/A | PVC | 0.191 in. | Black, Blue, Green, Gray, Orange, Pink, White, Yellow | 300V | `-20 to 60 C | UL 1666 | CMR | Yes | 25 lbs | 0.955 in. | 21 lbs | 26 Ohms/1000ft | 14 pF/ft | N/A | Networking, Security | #VALUE!
N4P245ES | CATEGORY 5E CMR 4 PAIR SHIELDED | Networking/LAN | 8 | 24 AWG | Solid | Bare Copper | Polyolefin | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | N/A | N/A | N/A | PVC | 0.252 in. | Blue | 300V | `-20 to 60 C | UL 1666 | CMR | Yes | 35 lbs | 1.260 in. | 29 lbs | 26 Ohms/1000ft | 15 pF/ft | N/A | Networking, Security | #VALUE!
N4P245EOSP | CATEGORY 5E OUTDOOR 4 PAIR | Networking/LAN | 8 | 24 AWG | Solid | Bare Copper | Polyolefin | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | N/A | N/A | N/A | UV Resistant Polyethylene | 0.255 in. | Black | 300V | `-20 to 60 C | None | N/A | Yes | 35 lbs | 1.275 in. | 34 lbs | 26 Ohms/1000ft | 14 pF/ft | N/A | Networking, Security | #VALUE!
N4P236A | CATEGORY 6A CMR 4 PAIR | Networking/LAN | 8 | 23 AWG | Solid | Bare Copper | Polyolefin | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | N/A | N/A | N/A | PVC | 0.260 in. | Black | 300V | `-20 to 60 C | UL 1666 | CMR | Yes | 25 lbs | 1.300 in. | 37 lbs | 24 Ohms/1000ft | 16 pF/ft | N/A | Networking, Security | #VALUE!
N4P236AS | CATEGORY 6A CMP 4 PAIR SHIELDED | Networking/LAN | 8 | 23 AWG | Solid | Bare Copper | Polyolefin | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | Overall Aluminum Foil | Tinned Copper | 24 AWG | PVC | 0.265 in. | Black | 300V | `-20 to 60 C | UL 1666 | CMR | Yes | 25 lbs | 1.325 in. | 37 lbs | 24 Ohms/1000ft | 16 pF/ft | N/A | Networking, Security | #VALUE!
N4P236 | CATEGORY 6 CMR 4 PAIR | Networking/LAN | 8 | 23 AWG | Solid | Bare Copper | Polyolefin | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | N/A | N/A | N/A | PVC | 0.220 in. | Black, Blue, Green, Gray, Orange, Violet, White, Yellow | 300V | `-20 to 60 C | UL 1666 | CMR | Yes | 40 lbs | 1.100 in. | 29 lbs | 24 Ohms/1000ft | 15 pF/ft | N/A | Networking, Security | #VALUE!
N4P236S | CATEGORY 6 CMR 4 PAIR SHIELDED | Networking/LAN | 8 | 23 AWG | Solid | Bare Copper | Polyolefin | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | Overall Aluminum Foil | Tinned Copper | 24 AWG | PVC | 0.275 in. | black | 300V | `-20 to 60 C | UL 1666 | CMR | Yes | 25 lbs | 1.100 in. | 37 lbs | 24 Ohms/1000ft | 13 pF/ft | N/A | Networking, Security | #VALUE!
WBN4P236 | CATEGORY 6 CM INDOOR/OUTDOOR 4 PAIR | Networking/LAN | 8 | 23 AWG | Solid | Bare Copper | Polyolefin | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | N/A | N/A | N/A | UV Resistant Polyethylene | 0.251 in. | Black | 300V | `-20 to 60 C | UL 1685 | CM-LS | Yes | 35 lbs | 1.255 in. | 43 lbs | 22 Ohms/1000ft | 14 pF/ft | N/A | Networking, Security | #VALUE!
N4P236OSP | CATEGORY 6 OUTDOOR 4 PAIR | Networking/LAN | 8 | 23 AWG | Solid | Bare Copper | Polyolefin | .010 in. | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN | N/A | N/A | N/A | UV Resistant Polyethylene | 0.255 in. | Black | 300V | `-20 to 60 C | None | N/A | Yes | 35 lbs | 1.275 in. | 39 lbs | 24 Ohms/1000ft | 14 pF/ft | N/A | Networking, Security | #VALUE!

## Category Cable Template
N4P236PS
Cable Description | CATEGORY 6 CMP 4 PAIR SHIELDED
Cable Use Applications | Networking, Security
Core Characteristics
Number of Conductors | 8
Gauge Size | 23 AWG
Stranding | Solid
Conductor Type | Bare Copper
Nominal Resistance | 24 Ohms/1000ft
Insulation Type | Flouropolymer
Insulation Thickness | .010 in.
Insulation Color Code | BL, WH/BL, OR, WH/OR, GN, WH/GN, BN, WH/BN
Shielding Characteristics
Shielding | Overall Aluminum Foil
Shielding Drain | Tinned Copper
Nominal Capacitance - Conductor to Conductor | 13 pF/ft
Nominal Capacitance - Conductor to Shield | N/A
Product Characteristics
Jacket Type | PVC
Overall Diameter | 0.255 in.
Standard Jacket Color | Black
Voltage Rating | 300V
Operating Temperature | `-20 to 60 C
Flame Test | NFPA 262
NEC Rating | CMP
RoHS Compliant | Yes
Max Pull Tension | 25 lbs
Max Bend Radius | 1.105 in.
Cable Weight | 37 lbs
#VALUE!

## Access Control - Life Safety
Part Number | Description | Cable Type | # of Condctors | # of Individual cables | Copper Type | Insulation color Code | Shielding | Jacket Type | Jacket Thickness | Nominal Cable O.D. | Jacket Colors | Voltage Rating | Operating Temperature | Flame Test | NEC Rating | RoHS Compliant | Max Pull Tension | Max Bend Radius | Cable Weight | Applications | Cable Print | Door Contact | Lock Power | Request to Exit | Card Reader
AC18223PP | Access Control - 4 Element - 3 Pair Reader | LSS/Access Control | 16 | 4 | Bare | BK, RD, WH, GN, BN, BL | 3 Pair Overall 100% AL Foil | Plenum PVC | 0.025 in. | 0.440 in. | YE | 300 V | `-20 to 60 C | NFPA 262 Plenum | CMP | Yes | 181 lbs | 4.4 in. | 98 lbs | Audio, Control, Low Voltage Power |  | 2C22P | 4C18P | 4C22P | 3P22PS
AC1822P | Access Control - 4 Element | LSS/Access Control | 16 | 4 | Bare | BK, RD, WH, GN, BN, BL | 6 conductor Overall 100% AL Foil | Plenum PVC | 0.025 in. | 0.440 in. | YE | 300 V | `-20 to 60 C | NFPA 262 Plenum | CMP | Yes | 181 lbs | 4.35 in. | 98 lbs | Audio, Control, Low Voltage Power |  | 2C22P | 4C18P | 4C22P | 6C22PS

## AC-LS Template
AC18223PP
Cable Description | Access Control - 4 Element - 3 Pair Reader
Cable Use Applications | Audio, Control, Low Voltage Power
Product Characteristics
Number of Conductors | 16
Number of Individual Cables | 4
Jacket Type | Plenum PVC
Jacket Thickness | 0.025 in.
Overall Diameter | 0.440 in.
Standard Jacket Color | YE
Voltage Rating | 300 V
Operating Temperature | `-20 to 60 C
Flame Test | NFPA 262 Plenum
NEC Rating | CMP
RoHS Compliant | Yes
Max Pull Tension | 181 lbs
Max Bend Radius | 4.4 in.
Cable Weight | 98 lbs
*For individual cable specifics see the following specification sheets
2C22P
4C18P
4C22P
3P22PS